## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.1d based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number
Date | 2015-03-20 16:04:08
Manufacturer Name | SMA America Production LLC
Product Name | SUNNY TRIPOWER
Product Models | STP 12000TL-US-10, STP 15000TL-US-10, STP 20000TL-US-10, STP 24000TL-US-10, STP 30000TL-US-10
Product Description | Utility interactive 3-phase inverter, Engineered in Germany – Assembled in USA

## Testing Info
Submitter | Georg Engelhard
Email | georg.engelhard@sma.de
Phone | 49 561 9522-2152
Interface Type | TCP
IP Address
IP Port | 502
Slave Id | 126

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | SMA | R
40020 | Model (Md) |  |  | Solar Inverter | R
40036 | Options (Opt) |  |  | 9197 | R
40044 | Version (Vr) |  |  | 40896003 | R
40052 | Serial Number (SN) |  |  | 191200204 | R
40068 | Device Address (DA) |  |  | unimplemented | RW
40069 | Pad |  |  |  | R

## 11
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 11
40071 | L |  |  | 13
40072 | Ethernet Link Speed (Spd) |  |  | supported | R
40073 | Interface Status Flags (CfgSt) |  |  | supported | R
|  |  | link status (LINK) | supported
|  |  | duplex (FULL_DUPLEX) | supported
|  |  | auto negotiation 1 (AUTO_NEG1) | unimplemented
|  |  | auto negotiation 2 (AUTO_NEG2) | unimplemented
|  |  | auto negotiation 3 (AUTO_NEG3) | unimplemented
|  |  | reset required (RESET_REQUIRED) | unimplemented
|  |  | hw fault (HW_FAULT) | unimplemented
40074 | Link State (St) |  |  | supported | R
|  |  | unknown (UNKNOWN) | supported
|  |  | enabled (ENABLED) | supported
|  |  | disabled (DISABLED) | supported
|  |  | testing (TESTING) | unimplemented
40075 | MAC |  |  | supported | R
40079 | Name (Nam) |  |  | unimplemented | RW
40083 | Control (Ctl) |  |  | unimplemented | RW
|  |  | auto (AUTO) | unimplemented
|  |  | duplex (FULL_DUPLEX) | unimplemented
40084 | Forced Speed (FrcSpd) |  |  | unimplemented | RW

## 12
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40085 | ID |  |  | 12
40086 | L |  |  | 98
40087 | Name (Nam) |  |  | unimplemented | RW
40091 | Config Status (CfgSt) |  |  | supported | R
|  |  | not configured (NOT_CONFIGURED) | unimplemented
|  |  | valid setting (VALID_SETTING) | supported
|  |  | valid hardware (VALID_HW) | unimplemented
40092 | Change Status (ChgSt) |  |  | supported | R
|  |  | pending (PENDING) | unimplemented
40093 | Config Capability (Cap) |  |  | supported | R
|  |  | DHCP | supported
|  |  | BOOTP | unimplemented
|  |  | zeroconf (ZEROCONF) | supported
|  |  | DNS | unimplemented
|  |  | configurable (CFG_SETTABLE) | unimplemented
|  |  | hw (HW_CONFIG) | unimplemented
|  |  | ntp (NTP_CLIENT) | unimplemented
|  |  | reset required (RESET_REQUIRED) | unimplemented
40094 | IPv4 Config (Cfg) |  |  | supported | RW
|  |  | static (STATIC) | supported
|  |  | DHCP | supported
|  |  | BOOTP | unimplemented
|  |  | zeroconf (ZEROCONF) | unimplemented
40095 | Control (Ctl) |  |  | supported | RW
|  |  | DNS (ENABLE_DNS) | supported
|  |  | NTP (ENABLE_NTP) | unimplemented
40096 | IP (Addr) |  |  | supported | RW
40104 | Netmask (Msk) |  |  | supported | RW
40112 | Gateway (Gw) |  |  | supported | RW
40120 | DNS1 |  |  | supported | RW
40128 | DNS2 |  |  | unimplemented | RW
40136 | NTP1 |  |  | unimplemented | RW
40148 | NTP2 |  |  | unimplemented | RW
40160 | Domain (DomNam) |  |  | unimplemented | RW
40172 | Host Name (HostNam) |  |  | unimplemented | RW
40184 | Pad |  |  |  | R

## 103
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40185 | ID |  |  | 103
40186 | L |  |  | 50
40187 | Amps (A) |  |  | unimplemented | R
40188 | Amps PhaseA (AphA) |  |  | supported | R
40189 | Amps PhaseB (AphB) |  |  | supported | R
40190 | Amps PhaseC (AphC) |  |  | supported | R
40191 | A_SF |  |  | -1 | R
40192 | Phase Voltage AB (PPVphAB) |  |  | unimplemented | R
40193 | Phase Voltage BC (PPVphBC) |  |  | unimplemented | R
40194 | Phase Voltage CA (PPVphCA) |  |  | unimplemented | R
40195 | Phase Voltage AN (PhVphA) |  |  | supported | R
40196 | Phase Voltage BN (PhVphB) |  |  | supported | R
40197 | Phase Voltage CN (PhVphC) |  |  | supported | R
40198 | V_SF |  |  | -1 | R
40199 | Watts (W) |  |  | supported | R
40200 | W_SF |  |  | 1 | R
40201 | Hz |  |  | supported | R
40202 | Hz_SF |  |  | -2 | R
40203 | VA |  |  | supported | R
40204 | VA_SF |  |  | 1 | R
40205 | VAr |  |  | supported | R
40206 | VAr_SF |  |  | 1 | R
40207 | PF |  |  | supported | R
40208 | PF_SF |  |  | -3 | R
40209 | WattHours (WH) |  |  | supported | R
40211 | WH_SF |  |  | 1 | R
40212 | DC Amps (DCA) |  |  | unimplemented | R
40213 | DCA_SF |  |  | unimplemented | R
40214 | DC Voltage (DCV) |  |  | unimplemented | R
40215 | DCV_SF |  |  | unimplemented | R
40216 | DC Watts (DCW) |  |  | unimplemented | R
40217 | DCW_SF |  |  | 2 | R
40218 | Cabinet Temperature (TmpCab) |  |  | unimplemented | R
40219 | Heat Sink Temperature (TmpSnk) |  |  | unimplemented | R
40220 | Transformer Temperature (TmpTrns) |  |  | unimplemented | R
40221 | Other Temperature (TmpOt) |  |  | unimplemented | R
40222 | Tmp_SF |  |  | 0 | R
40223 | Operating State (St) |  |  | unimplemented | R
|  |  | Off (OFF) | unimplemented
|  |  | Sleeping (SLEEPING) | unimplemented
|  |  | Starting (STARTING) | unimplemented
|  |  | MPPT | unimplemented
|  |  | Throttled (THROTTLED) | unimplemented
|  |  | Shutting down (SHUTTING_DOWN) | unimplemented
|  |  | Fault (FAULT) | unimplemented
|  |  | Standby (STANDBY) | unimplemented
40224 | Vendor Operating State (StVnd) |  |  | unimplemented | R
40225 | Event1 (Evt1) |  |  | supported | R
|  |  | Ground fault (GROUND_FAULT) | supported
|  |  | DC over voltage (DC_OVER_VOLT) | supported
|  |  | AC disconnect open (AC_DISCONNECT) | supported
|  |  | DC disconnect open (DC_DISCONNECT) | supported
|  |  | Grid shutdown (GRID_DISCONNECT) | supported
|  |  | Cabinet open (CABINET_OPEN) | supported
|  |  | Manual shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over temperature (OVER_TEMP) | supported
|  |  | Frequency above limit (OVER_FREQUENCY) | supported
|  |  | Frequency under limit (UNDER_FREQUENCY) | supported
|  |  | AC Voltage above limit (AC_OVER_VOLT) | supported
|  |  | AC Voltage under limit (AC_UNDER_VOLT) | supported
|  |  | Blown String fuse on input (BLOWN_STRING_FUSE) | supported
|  |  | Under temperature (UNDER_TEMP) | supported
|  |  | Generic Memory or Communication error (internal) (MEMORY_LOSS) | supported
|  |  | Hardware test failure (HW_TEST_FAILURE) | supported
40227 | Event Bitfield 2 (Evt2) |  |  | unimplemented | R
40229 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | unimplemented | R
40231 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | unimplemented | R
40233 | Vendor Event Bitfield 3 (EvtVnd3) |  |  | unimplemented | R
40235 | Vendor Event Bitfield 4 (EvtVnd4) |  |  | unimplemented | R

## 120
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40237 | ID |  |  | 120
40238 | L |  |  | 26
40239 | DERTyp |  |  | supported | R
|  |  | PV | supported
|  |  | PV_STOR | unimplemented
40240 | WRtg |  |  | supported | R
40241 | WRtg_SF |  |  | 2 | R
40242 | VARtg |  |  | supported | R
40243 | VARtg_SF |  |  | 2 | R
40244 | VArRtgQ1 |  |  | supported | R | Sign is reversed.
40245 | VArRtgQ2 |  |  | unimplemented | R | Contains a value of 0 instead of unimplemented value.
40246 | VArRtgQ3 |  |  | unimplemented | R | Contains a value of 0 instead of unimplemented value.
40247 | VArRtgQ4 |  |  | supported | R | Sign is reversed.
40248 | VArRtg_SF |  |  | 2 | R
40249 | ARtg |  |  | unimplemented | R
40250 | ARtg_SF |  |  | 0 | R
40251 | PFRtgQ1 |  |  | supported | R
40252 | PFRtgQ2 |  |  | supported | R
40253 | PFRtgQ3 |  |  | supported | R
40254 | PFRtgQ4 |  |  | supported | R
40255 | PFRtg_SF |  |  | -1 | R
40256 | WHRtg |  |  | unimplemented | R
40257 | WHRtg_SF |  |  | 2 | R
40258 | AhrRtg |  |  | unimplemented | R
40259 | AhrRtg_SF |  |  | 0 | R
40260 | MaxChaRte |  |  | unimplemented | R
40261 | MaxChaRte_SF |  |  | 2 | R
40262 | MaxDisChaRte |  |  | unimplemented | R
40263 | MaxDisChaRte_SF |  |  | 2 | R
40264 | Pad |  |  |  | R

## 121
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40265 | ID |  |  | 121
40266 | L |  |  | 30
40267 | WMax |  |  | supported | RW
40268 | VRef |  |  | supported | RW
40269 | VRefOfs |  |  | supported | RW
40270 | VMax |  |  | unimplemented | RW
40271 | VMin |  |  | unimplemented | RW
40272 | VAMax |  |  | supported | RW
40273 | VArMaxQ1 |  |  | unimplemented | RW
40274 | VArMaxQ2 |  |  | unimplemented | RW
40275 | VArMaxQ3 |  |  | unimplemented | RW
40276 | VArMaxQ4 |  |  | unimplemented | RW
40277 | WGra |  |  | supported | RW
40278 | PFMinQ1 |  |  | unimplemented | RW
40279 | PFMinQ2 |  |  | unimplemented | RW
40280 | PFMinQ3 |  |  | unimplemented | RW
40281 | PFMinQ4 |  |  | unimplemented | RW
40282 | VArAct |  |  | unimplemented | RW
|  |  | SWITCH | unimplemented
|  |  | MAINTAIN | unimplemented
40283 | ClcTotVA |  |  | unimplemented | RW
|  |  | VECTOR | unimplemented
|  |  | ARITHMETIC | unimplemented
40284 | MaxRmpRte |  |  | unimplemented | RW
40285 | ECPNomHz |  |  | unimplemented | RW
40286 | ConnPh |  |  | unimplemented | RW
|  |  | A | unimplemented
|  |  | B | unimplemented
|  |  | C | unimplemented
40287 | WMax_SF |  |  | 2 | R
40288 | VRef_SF |  |  | 0 | R
40289 | VRefOfs_SF |  |  | 0 | R
40290 | VMinMax_SF |  |  | -2 | R
40291 | VAMax_SF |  |  | 2 | R
40292 | VArMax_SF |  |  | 2 | R
40293 | WGra_SF |  |  | 0 | R
40294 | PFMin_SF |  |  | unimplemented | R
40295 | MaxRmpRte_SF |  |  | unimplemented | R
40296 | ECPNomHz_SF |  |  | 0 | R

## 122
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40297 | ID |  |  | 122
40298 | L |  |  | 44
40299 | PVConn |  |  | supported | R
|  |  | CONNECTED | supported
|  |  | AVAILABLE | supported
|  |  | OPERATING | supported
|  |  | TEST | unimplemented
40300 | StorConn |  |  | unimplemented | R
|  |  | CONNECTED | unimplemented
|  |  | AVAILABLE | unimplemented
|  |  | OPERATING | unimplemented
|  |  | TEST | unimplemented
40301 | ECPConn |  |  | unimplemented | R
|  |  | CONNECTED | unimplemented
40302 | ActWh |  |  | unimplemented | R
40306 | ActVAh |  |  | unimplemented | R
40310 | ActVArhQ1 |  |  | unimplemented | R
40314 | ActVArhQ2 |  |  | unimplemented | R
40318 | ActVArhQ3 |  |  | unimplemented | R
40322 | ActVArhQ4 |  |  | unimplemented | R
40326 | VArAval |  |  | unimplemented | R
40327 | VArAval_SF |  |  | unimplemented | R
40328 | WAval |  |  | unimplemented | R
40329 | WAval_SF |  |  | unimplemented | R
40330 | StSetLimMsk |  |  | unimplemented | R
|  |  | WMax | unimplemented
|  |  | VAMax | unimplemented
|  |  | VArAval | unimplemented
|  |  | VArMaxQ1 | unimplemented
|  |  | VArMaxQ2 | unimplemented
|  |  | VArMaxQ3 | unimplemented
|  |  | VArMaxQ4 | unimplemented
|  |  | PFMinQ1 | unimplemented
|  |  | PFMinQ2 | unimplemented
|  |  | PFMinQ3 | unimplemented
|  |  | PFMinQ4 | unimplemented
40332 | StActCtl |  |  | unimplemented | R
|  |  | FixedW | unimplemented
|  |  | FixedVAR | unimplemented
|  |  | FixedPF | unimplemented
|  |  | Volt-VAr | unimplemented
|  |  | Freq-Watt-Param | unimplemented
|  |  | Freq-Watt-Curve | unimplemented
|  |  | Dyn-Reactive-Current | unimplemented
|  |  | LVRT | unimplemented
|  |  | HVRT | unimplemented
|  |  | Watt-PF | unimplemented
|  |  | Volt-Watt | unimplemented
|  |  | Scheduled | unimplemented
|  |  | LFRT | unimplemented
|  |  | HFRT | unimplemented
40334 | TmSrc |  |  | unimplemented | R
40338 | Tms |  |  | unimplemented | R
40340 | RtSt |  |  | unimplemented | R
|  |  | LVRT_ACTIVE | unimplemented
|  |  | HVRT_ACTIVE | unimplemented
|  |  | LFRT_ACTIVE | unimplemented
|  |  | HFRT_ACTIVE | unimplemented
40341 | Ris |  |  | unimplemented | R
40342 | Ris_SF |  |  | 4 | R

## 127
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40461 | ID |  |  | 127
40462 | L |  |  | 10
40463 | WGra |  |  | supported | RW
40464 | HzStr |  |  | supported | RW
40465 | HzStop |  |  | supported | RW
40466 | HysEna |  |  | supported | RW
|  |  | ENABLED | supported
40467 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40468 | HzStopWGra |  |  | supported | RW
40469 | WGra_SF |  |  | 0 | R
40470 | HzStrStop_SF |  |  | -2 | R
40471 | RmpIncDec_SF |  |  | 0 | R
40472 | Pad |  |  |  | R

## 160
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40621 | ID |  |  | 160
40622 | L |  |  | 48
40623 | Current Scale Factor (DCA_SF) |  |  | -1 | R
40624 | Voltage Scale Factor (DCV_SF) |  |  | 0 | R
40625 | Power Scale Factor (DCW_SF) |  |  | 2 | R
40626 | Energy Scale Factor (DCWH_SF) |  |  | unimplemented | R
40627 | Global Events (Evt) |  |  | unimplemented | R
|  |  | Ground Fault (GROUND_FAULT) | unimplemented
|  |  | Input Over Voltage (INPUT_OVER_VOLTAGE) | unimplemented
|  |  | Reserved (RESERVED) | unimplemented
|  |  | DC Disconnect (DC_DISCONNECT) | unimplemented
|  |  | Cabinet Open (CABINET_OPEN) | unimplemented
|  |  | Manual Shutdown (MANUAL_SHUTDOWN) | unimplemented
|  |  | Over Temperature (OVER_TEMP) | unimplemented
|  |  | Blown Fuse (BLOWN_FUSE) | unimplemented
|  |  | Under Temperature (UNDER_TEMP) | unimplemented
|  |  | Memory Loss (MEMORY_LOSS) | unimplemented
|  |  | Arc Detection (ARC_DETECTION) | unimplemented
|  |  | Test Failed (TEST_FAILED) | unimplemented
|  |  | Under Voltage (INPUT_UNDER_VOLTAGE) | unimplemented
|  |  | Over Current (INPUT_OVER_CURRENT) | unimplemented
40629 | Number of Modules (N) |  |  | supported | R
40630 | Timestamp Period (TmsPer) |  |  | unimplemented | R
40631 | Input ID (ID) | 1 |  | supported | R
40632 | Input ID Sting (IDStr) | 1 |  | unimplemented | R
40640 | DC Current (DCA) | 1 |  | supported | R
40641 | DC Voltage (DCV) | 1 |  | supported | R
40642 | DC Power (DCW) | 1 |  | supported | R
40643 | Lifetime Energy (DCWH) | 1 |  | unimplemented | R
40645 | Timestamp (Tms) | 1 |  | unimplemented | R
40647 | Temperature (Tmp) | 1 |  | unimplemented | R
40648 | Operating State (DCSt) | 1 |  | unimplemented | R
|  |  | Off (OFF) | unimplemented
|  |  | Sleeping (SLEEPING) | unimplemented
|  |  | Starting (STARTING) | unimplemented
|  |  | MPPT | unimplemented
|  |  | Throttled (THROTTLED) | unimplemented
|  |  | Shutting Down (SHUTTING_DOWN) | unimplemented
|  |  | Fault (FAULT) | unimplemented
|  |  | Standby (STANDBY) | unimplemented
|  |  | Test (TEST) | unimplemented
|  |  | Reserved (RESERVED) | unimplemented
40649 | Module Events (DCEvt) | 1 |  | unimplemented | R
|  |  | Ground Fault (GROUND_FAULT) | unimplemented
|  |  | Input Over Voltage (INPUT_OVER_VOLTAGE) | unimplemented
|  |  | Reserved (RESERVED) | unimplemented
|  |  | DC Disconnect (DC_DISCONNECT) | unimplemented
|  |  | Cabinet Open (CABINET_OPEN) | unimplemented
|  |  | Manual Shutdown (MANUAL_SHUTDOWN) | unimplemented
|  |  | Over Temperature (OVER_TEMP) | unimplemented
|  |  | Blown Fuse (BLOWN_FUSE) | unimplemented
|  |  | Under Temperature (UNDER_TEMP) | unimplemented
|  |  | Memory Loss (MEMORY_LOSS) | unimplemented
|  |  | Arc Detection (ARC_DETECTION) | unimplemented
|  |  | Test Failed (TEST_FAILED) | unimplemented
|  |  | Under Voltage (INPUT_UNDER_VOLTAGE) | unimplemented
|  |  | Over Current (INPUT_OVER_CURRENT) | unimplemented
40651 | Input ID (ID) | 2 |  | supported | R
40652 | Input ID Sting (IDStr) | 2 |  | unimplemented | R
40660 | DC Current (DCA) | 2 |  | supported | R
40661 | DC Voltage (DCV) | 2 |  | supported | R
40662 | DC Power (DCW) | 2 |  | supported | R
40663 | Lifetime Energy (DCWH) | 2 |  | unimplemented | R
40665 | Timestamp (Tms) | 2 |  | unimplemented | R
40667 | Temperature (Tmp) | 2 |  | unimplemented | R
40668 | Operating State (DCSt) | 2 |  | unimplemented | R
40669 | Module Events (DCEvt) | 2 |  | unimplemented | R